## Slide 1
Design of an Intelligent Energy Management System for a Hybrid Microgrid with Renewables and Battery Storage
Ntokozo Radebe (supervised by A/Prof Sunetra Chowdhury)

## Slide 2: Content
Initial Situation
Load Data
System Components
Algorithm
Results
Conclusion

## Slide 3: Initial situation:

## Slide 4: Situation
Context
Global energy shift is creating a rising demand for sustainable, decentralized power systems.
Design requirements
Hybrid microgrids are a solution to this demand, combining renewable energy sources and traditional energy sources, able to operate both grid-connected and standalone.
Intermittency of renewable generators (solar PV) create supply-demand imbalances
Need for intelligent energy management systems to ensure stability and cost efficiency arises
Minimize cost of energy draw from the utility grid during grid-connected
Optimum use of solar PV and BESS as renewable energy sources
Ensure energy security during standalone mode
Ensure power quality at the load terminals in both operating modes

## Slide 5: Literature Review
Algorithms reviewed
Algorithms used in the models studied:
Classical algorithms
Metaheuristic algorithms
Intelligent algorithms
  Fuzzy logic
  Artificial Neural Network
  Deep Learning
Algorithms and their functions
Roles and priorities of the algorithms were:
Prioritize price
Prioritize sizing of microgrid
Ensure voltage control
Perform
  Peak shaving
  Curtailment

## Slide 6: Load Data:

## Slide 7: Data
Load Characteristics:
Load Characteristic | Energy (KWh)
Total | 4326
Average | 180
Maximum | 206.4
Minimum | 153

## Slide 8: Load Profiles
Original sized load
Increased load (additional constant load)

## Slide 9: System components:

## Slide 10: Solar Photovoltaic Panels (PV)
Key considerations
+ Use of NASA Power Data to obtain weather data
+ Radiance data and temperature data to calculate power losses (STC concept)
+ Area is 2000m^2, efficiency of panels is 18%
+ IEC 62548
+ Total size is 472.43 kW
Notes: STC – Standard Test Condition
NOCT – Nominal Operating Cell Temperature

## Slide 11: Utility grid
Key considerations
+ Use of utility grid based on low TOU tariff periods.
+ Sized to export maximum of 500 MW, with voltage of integration of 400 V.
+ IEEE1547

## Slide 12: Battery Energy Storage System
+ Storage capacity is 3000kWh, terminal voltage 400V.
+ Min and Max SOC of 30% to 90% extend battery life
+ FLC IEMS integrated with the BESS to schedule charging and discharging commands.
+ Sized to be able to absorb all PV surplus power.
Minimum dis/charge time | 10 hours
Maximum power | 300 kW
Maximum SOC | 90%
Minimum SOC | 30%
Dis/charging efficiency | 95%
Battery inverter efficiency | 96%

## Slide 13: The Algorithm:

## Slide 14: High level Flow Diagram

## Slide 15: Fuzzy Logic
Mamdani FLC for BESS control
Controls the charging and discharging pattern
Sugeno FLC for mode and load control
Controls mode of operation and load connection

## Slide 16: Integration:

## Slide 17: Microgrid with FLC IEMS

## Slide 18: Results:

## Slide 19: Simulation – Observations
Case 3 grid power, TOU tariff and grid cost of energy
Case 4 grid power, TOU tariff and grid cost of energy

## Slide 20: Simulation – Standard sized conditions

## Slide 21: Simulation – Increased load

## Slide 22: Results - Total Load Demand
Chart: Distributed energy resource contribution to load
| Case 1 | Case 2 | Case 3 | Case 4
Utility grid | 39.5959 | 11.7487 | 28.9364 | 43.5986
Solar PV | 60.4041 | 60.4041 | 60.4041 | 47.0344
BESS | 0 | 28.2861 | 11.3818 | 9.6835
Chart: Renewable Factor (RF)
| Case 1 | Case 2 | Case 3 | Case 4
 | 0.3445 | 0.8675 | 0.5969 | 0.2313

## Slide 23: Results - Total Cost of Energy
Chart: Cost of Energy
| Case 1 | Case 2 | Case 3 | Case 4
 | 4437 | 2317 | 1312 | 2711
+ Highest cost of energy from the utility grid was R4437.00, due to no FLC IEMS and BESS integration.
+ Best case of R1312.00 was achieved for the CoE due to implemented FLC IEMS with BESS.

## Slide 24: Conclusion:

## Slide 25: + Relevant since the power systems had more than 1 resource
Key takeaways, the FLC IEMS was…
+ Necessary with hybrid renewable energy systems
+ Used for cost reduction and satisfying demand by ensuring optimum use of DERs
+ Diﬀerent strategies for controls functions
+ Ensure the power quality at the load terminals by ensuring minimal frequency fluctuations and voltage fluctuations doing DER power flow

## Slide 26: THANK YOU!